## Sheet1
Diagnostic | Code Message
code | AFDD-1 (Temperature Sensor Fault)
20 | No faults detected
21 | Temperature sensor fault
22 | Conditions not favorable for diagnostic
23 | Mixed-air temperature outside of expected range
24 | Return-air temperature outside of expected range
25 | Outside-air temperature outside of expected range
27 | Missing data necessary for fault detection
29 | Unit is off (No Fault)
AFDD-2 (Unit Economizing When it Should)
30 | No faults detected
31 | Unit is not currently cooling or conditions are not favorable for economizing (No Fault)
32 | Insufficient outdoor air when economizing (Fault)
33 | Outdoor-air damper is not fully open when the unit should be economizing (Fault)
36 | OAD is open but conditions were not favorable for OAF calculation (No Fault)
37 | Missing data necessary for fault detection (No Fault)
38 | OAD is open when economizing but OAF calculation led to an unexpected value (No Fault)
39 | Unit is off (No Fault)
AFDD-3 (Unit Economizing When it Should)
40 | No faults detected
41 | Damper should be at minimum position but is not (Fault)
43 | Conditions favorable for economizing (No Fault)
47 | Missing data necessary for fault detection (No Fault)
49 | Unit is off (No Fault)
AFDD-4 (Excess Outdoor-air Intake)
50 | No faults detected
51 | Excessive outdoor-air intake
52 | Damper is at minimum but conditions are not favorable for OAF calculation (No Fault)
53 | Damper is not at minimum (Fault)
56 | Unit should be economizing (No Fault)
57 | Missing data necessary for fault detection (No Fault)
58 | Damper is at minimum but OAF calculation led to an unexpected value (No Fault)
59 | Unit is off (No Fault)
AFDD-5 (Insufficient Outdoor-air Ventilation)
60 | No faults detected
61 | Insufficient outdoor-air intake (Fault)
62 | Damper is at minimum but conditions are not favorable for OAF calculation (No Fault)
63 | Damper is not at minimum when is should not be (Fault)
66 | Unit should be economizing (No Fault)
67 | Missing data necessary for fault detection (No Fault)
68 | Damper is at minimum but conditions are not favorable for OAF calculation (No Fault)
69 | Unit is off (No Fault)
AFDD-6 (Schedule)
70 | Unit is operating correctly based on input on/off time (No Fault)
71 | Unit is operating at a time designated in schedule as "off" time
77 | Missing data